## Tests
Test | Commercial Test Table 4 |  | Commercial Test Table 5 |  | Commercial Test BG50 Table 1
Test Parameters
pH | 6.6 -8.5 | recommended range (6.6 to 8.5) (F1 affects) | 6.6 -8.5 | recommended range (6.6 to 8.5) (F1 affects) | 6.6 -8.5 | recommended range (6.6 to 8.5) (F1 affects)
Conductivity uS/cm | Greater than Mains | recommend greater than mains (F1 affects) | Greater than Mains | recommend greater than mains (F1 affects) | Greater than Mains | recommend greater than mains (F1 affects)
Total hardness as CaC03 mg/L |  |  |  |  | maintained | less than 30% drop from makeup water / no significant change from previous
Hardness deposition % |  |  |  |  | maintained | less than 30% drop from makeup water / no significant change from previous
M - alkalinity as CaC03 mg/L | Greater than(300mg/l) | as CaCO3 recommended >(300mg/l) (F1 affects) | Greater than(300mg/l) | as CaCO3 recommended >(300mg/l) (F1 affects)
Aluminium mg/L |  |  |  |  | Less than (1mg/l | Less than (1mg/l
Iron mg/L | Less than (6mg/l) | less than (6mg/l) | Less than (6mg/l) | less than (6mg/l) | Less than (1mg/l | Less than (1mg/l
Copper mg/L | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l)
Phosphorous mg/L |  |  |  |  | competitor product | should be absent with F1, varys with competitors (typically >100mg/l)
Molybdenum mg/L |  |  |  |  | used to calc Molybdate
Chloride mg/L | Less than (50mg/l) | as CI recommended <(50mg/l) over make up water | Less than (50mg/l) | as CI recommended <(50mg/l) over make up water
Excess Chloride mg/L
Sulphates mg/L | Greater than (90%) | as SO4 recommended >(90%) make water, with no increasing trend | Greater than (90%) | as SO4 recommended >(90%) make water, with no increasing trend | Greater than (90%) | as SO4 recommended >(90%) make water, with no increasing trend
Refractive Index |  |  |  | if present, dependant on treatment
% Monopropylene Glycol |  |  |  | if present, dependant on treatment |  | if present, dependant on treatment
German Degrees Hardness | N/A |  | N/A |  | N/A | N/A
Sebacate mg/L | N/A |  | N/A
Nitrate mg/L |  |  |  |  | competitor product | used by competitors as an Aluminium inhibitor, or by oxidation of Nitrite
Total Dissolved Solids (Calculated) mg/L | Greater than Mains | recommend greater than mains, with no increasing trend (F1 affects) | Greater than Mains | recommend greater than mains, with no increasing trend (F1 affects)
Suspended Solids mg/L | Less than (30mg/l) | less than (30mg/l) generally, less than (45mg/l) at extremities / termination points | Less than (30mg/l) | less than (30mg/l) generally, less than (45mg/l) at extremities / termination points
Total Iron mg/L | less than (6mg/l) | less than (6mg/l) | less than (15mg/l) | less than (15mg/l) | less than (25mg/l) | less than (25mg/l)
Total Copper mg/L | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l)
Nitrite mg/L | competitor product | should be absent with F1, if competitor then >500mg/l | competitor product | should be absent with F1, if competitor then >500mg/l | competitor product | should be absent with F1, if competitor then >500mg/l
Molybdate mg/L | 110mg/l | 110mg/l when first dosed, decreases with time due to being consumed | 110mg/l | 110mg/l when first dosed, decreases with time due to being consumed | 110mg/l | 110mg/l when first dosed, decreases with time due to being consumed
Total Aluminium mg/L | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l)
Total Zinc mg/L |  |  | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l) | Less than (1mg/l)
Total Zinc |  |  |  |  | Less than (1mg/l) | Less than (1mg/l)
Amonia mg/L

## Recommendations
| Ideal Result | Guideline | Example Result | Recommendations | Product Code
Visual Appearance | 1 | 0 = Clear, 1 = slightly cloudy, 2 = cloudy, 3 = Very cloudy/settled solids (<2) | 3 | Side stream filtration and Protector F9 | F9 - 62557 10L
M-alkalinity (mg/l CaCO3) (total alkalinity) | 1100 | >300mg/l | <300mg/l | Check level of Alkalinity, if low increase Protector F1 level | F1 - 62554 10L
P-alkalinity (mg/l CaCO3) | 0 | no increasing trend | 10mg/l to 20mg/l | Trend increasing from base test, increase Protector F1 level | F1 - 62554 10L
Chloride (mg/l Cl) | 34 | <50mg/l greater than makeup | 50mg/l to 60mg/l | Trend increasing from base and no Biocide present, treat with Cleaner F3 and Protector F1 | F1 - 62554 10L F3 - 62555 10L
Sulphate (mg/l SO4) | 42 | >90% greater than makeup with no increasing trend | 42mg/l to 38mg/l | Trend decreasing from base test, treat with Biocide F7+ | F7+ - 62598 10L
Conductivity (µS/cm) | 1200 | no sudden drop from previous sample | 1100µS/cm | Check for leaks or accidental discharge and treat with Protector F1 | F1 - 62554 10L
Total Dissolved Solids (mg/l) | 852 | no sudden drop from previous sample | 800mg/l | Check for leaks or accidental discharge and treat with Protector F1 | F1 - 62554 10L
Suspended Solids (mg/l) | 12 | Less than 30 mg/l at system pump during circulation | 35mg/l | Side stream filtration and Protector F9 | F9 - 62557 10L
pH | 8.3 | 6.6 to 8.5 ideal pH level | 6.2 or 8.9 | If low pH Clean with F3, Flush and Protector F1. If high, check Protector level and increase Protector F1 level to bring down to recommended levels. Also sidestream filtration and Protector F9 should be considered to maintain system | F1 - 62554 10L F3 - 62555 10L
Ammonia as NH3 | 0 | no increasing trend | 2NH₃ to 4NH₃ | Recommend NRB testing and if necessary treat with Biocide F7+, If no NRB's consider Cleaner F3 and Protector F1 | F1 - 62554 10L F3 F7+ - 62598 10L
Molybdenum | 98 | greater than 60mg/l | 50mg/l | If lower than recommended levels and a decreasing trend, top up with Protector F1 | F1 - 62554 10L
Dissolved iron (mg/l) | 1 | Less than 3 mg/l | 5mg/l | increasing trend indicates corrosion, Check Protector F1 level and increase. If no retardation in trend, treat with Cleaner F3 and retreat with Protector F1. | F1 - 62554 10L F3 - 62555 10L
Total iron (mg/l) | 1 | Less than 25 mg/l | 30mg/l | increasing trend indicates corrosion, Check Protector F1 level and increase. If no retardation in trend, treat with Cleaner F3 and retreat with Protector F1. | F1 - 62554 10L F3 - 62555 10L
Dissolved copper (mg/l) | 0 | Less than 1 mg/l | 5mg/l | increasing trend indicates corrosion, Check Protector F1 level and increase. If no retardation in trend, treat with Cleaner F3 and retreat with Protector F1. | F1 - 62554 10L F3 - 62555 10L
Total copper (mg/l) | 0 | Less than 1 mg/l | 5mg/l | increasing trend indicates corrosion, Check Protector F1 level and increase. If no retardation in trend, treat with Cleaner F3 and retreat with Protector F1. | F1 - 62554 10L F3 - 62555 10L
Total aluminium (mg/l) | 0 | Less than 1 mg/l | 5mg/l | increasing trend indicates corrosion, Check Protector F1 level and increase. If no retardation in trend, treat with Cleaner F3 and retreat with Protector F1. | F1 - 62554 10L F3 - 62555 10L
Total Zinc (mg/l) | 0 | Less than 1 mg/l | 5mg/l | increasing trend indicates corrosion, Check Protector F1 level and increase. If no retardation in trend, treat with Cleaner F3 and retreat with Protector F1. | F1 - 62554 10L F3 - 62555 10L